Location:	
Engineer:	
Study Case:   LF
12.6.0H
Page:	1 
SN:    	
Filename:	terdahulu2
Project:	

 
ETAP 
Contract:	  
Date:	08-22-2018 
Revision:	Base
Config.: 	KONDISI 1
Bus Loading Summary Report
ID
Bus
kV
Directly Connected Load
% PF
Amp

Rated Amp
Loading
Constant kVA
Constant Z
Constant I
Percent
Generic
Total Bus Load
kvar
kW
kvar
kW
kvar
kW
kvar
kW
kVA
BUS CLUSTER A
 0.400
 13.2
 91.1
 2.2
 0.0
 6.0
 3.7
 0.0
 0.0
 0.0
 0.0
 9.1
BUS CLUSTER B
 0.400
 13.2
 91.1
 2.2
 0.0
 6.0
 3.7
 0.0
 0.0
 0.0
 0.0
 9.1
BUS CLUSTER C
 0.400
 132.0
 86.4
 23.1
 10.2
 38.7
 27.8
 0.0
 0.0
 0.0
 0.0
 90.6
BUS CLUSTER D
 0.400
 400.0
 14.2
 56.6
 89.5
 7.7
 1.8
 19.7
 12.2
 0.0
 0.0
 0.0
 0.0
 39.2
BUS CLUSTER F
 0.400
 12.2
 91.1
 2.1
 0.0
 5.6
 3.5
 0.0
 0.0
 0.0
 0.0
 8.4
BUS CLUSTER H
 6.300
 12.3
 86.6
 0.0
 0.0
 0.0
 0.0
 0.0
 0.0
 0.0
 0.0
 133.8
Bus1
 20.000
 3.9
 87.0
 0.0
 0.0
 0.0
 0.0
 0.0
 0.0
 0.0
 0.0
 131.7
* Indicates operating load of a bus exceeds the bus critical limit ( 100.0%  of  the Continuous Ampere rating).
# Indicates operating load of a bus exceeds the bus marginal limit ( 90.0%  of  the Continuous Ampere rating).

Location:	
Engineer:	
Study Case:   LF
12.6.0H
Page:	2 
SN:    	
Filename:	terdahulu2
Project:	 
ETAP 
Contract:	  
Date:	08-22-2018 
Revision:	Base
Config.: 	KONDISI 1
Branch Loading Summary Report
ID
Type
Loading
Amp
%
%
Loading (output) 
CKT / Branch
Cable & Reactor
Transformer
Loading (input) 
%
Ampacity
(Amp)
Capability
(kVA)
kVA
kVA
C-TR-01
Transformer
 44.6
 43.9
 300.0
 133.8
 131.7
C-TR-O2
Transformer
 46.1
 45.3
 200.0
 92.2
 90.6
D-TR-01
Transformer
 24.7
 24.5
 160.0
 39.6
 39.2
*   Indicates a branch with operating load exceeding the branch capability.

Location:	
Engineer:	
Study Case:   LF
12.6.0H
Page:	3 
SN:    	
Filename:	terdahulu2
Project:	 
ETAP 
Contract:	  
Date:	08-22-2018 
Revision:	Base
Config.: 	KONDISI 1
Branch Losses Summary Report
ID
kW
kvar
From
To
CKT / Branch
From-To Bus Flow
To-From Bus Flow
Losses
% Bus Voltage
%  Drop 
Vd
in Vmag
kW
kvar
kW
kvar
 1.0
 1.5
 99.1
 98.4
 0.73
C-TR-O2
‑45.6
‑45.6
 47.0
 47.0
 0.2
 0.4
 99.9
 98.4
 1.46
D-TR-01
‑17.5
‑17.5
 17.9
 17.9
 1.3
 2.0
 100.0
 98.4
 1.60
C-TR-01
 66.9
 66.9
‑64.9
‑64.9
 2.5
 3.8

Location:	
Engineer:	
Study Case:   LF
12.6.0H
Page:	4 
SN:    	
Filename:	terdahulu2
Project:	 
ETAP 
Contract:	  
Date:	08-22-2018 
Revision:	Base
Config.: 	KONDISI 1
Alert Summary Report
Cable
 95.0
 100.0
Bus
Marginal
Critical
 90.0
 100.0
Loading
% Alert Settings
 95.0
 100.0
 95.0
 100.0
 95.0
 100.0
Line
Transformer
Reactor
Panel
 95.0
 100.0
 90.0
 95.0
 102.0
 105.0
 95.0
 100.0
 95.0
 100.0
 95.0
 100.0
100.0
Generator Excitation
Bus Voltage
UnderExcited (Q Min.)
OverExcited (Q Max.)
UnderVoltage
OverVoltage
Protective Device
Generator
Inverter/Charger
 100.0
 95.0

Location:	
Engineer:	
Study Case:   LF
12.6.0H
Page:	5 
SN:    	
Filename:	terdahulu2
Project:	 
ETAP 
Contract:	  
Date:	08-22-2018 
Revision:	Base
Config.: 	KONDISI 1
 0.0
 0.0
 3.8
 2.5
 0.0
 0.0
 0.0
 0.0
 0.0
 0.0
 91.6
 51.0
 76.1
 39.2
 12.1
 37.3
 133.8
 66.9
 115.9
 0.0
 0.0
 133.8
 66.9
 0.0
 115.9
kVA
kvar
kW
Lagging
 83.07
Total Generic Load:
Total Constant I Load:
Number of Iterations:   1
System Mismatch:
Apparent Losses:
SUMMARY  OF  TOTAL  GENERATION ,  LOADING  &  DEMAND
Lagging
 95.15
Lagging
Lagging
 86.62
 86.62
% PF
Total Static Load:
Total Motor Load:
Total Demand:
Source (Non-Swing Buses):
Source (Swing Buses):